Mr. Stephen Vaughan, Plan it Design, Cae Llwyndu, Nelson. CF64 6HX

Dear Sir,

Building Regulations 2010 : Regulation 14

Full Plans Application

12, Romilly Avenue, Barry

Construct a two storey rear extension and rear ground floor balcony

Under the Building Regulations 2010 your application for the above mentioned proposed works has been approved.

Please be advised that the Vale of Glamorgan Council can issue (upon satisfactory completion of building work) a completion certificate.  Possession of such a certificate is essential, especially when selling your property at a future date.  It also ensures your builder's obligation to comply with the requirements of the Building Regulations.

It is vitally important that before you finalise transactions with your builder, you ensure that the Building Control Officer carries out the final inspection and is satisfied that all relevant inspections have been undertaken.

If a completion certificate is not received by you within seven days of inspection, or you have a query on Building Regulation procedures please do not hesitate to contact the Building Control Section on the above telephone number.

PLEASE NOTE

Some forms of building work could invoke proceedings under The Party Wall etc. Act, 1996.  If you are uncertain of your position you are advised to consult a surveyor.

Yours faithfully,

Mr. D. D. Williams

for Operational Manager Development & Building Control

Reference: 2014/0864/BR

T H E   V A L E   O F   G L A M O R G A N   C O U N C I L

Building Act 1984

Building Regulations 2010

# FULL PLANS APPROVAL NOTICE

| Agent: Mr. Stephen Vaughan, Plan it Design, Cae Llwyndu, Nelson. CF64 6HX | Applicant: Mr. Alun Williams, 12, Romilly Avenue, Barry, Vale of Glamorgan. CF62 6RB |
| --- | --- |

Details of work:	Construct a two storey rear extension and rear ground floor balcony

Location:	12, Romilly Avenue, Barry

The plans received on 23 December 2014 in respect to the above work have been examined and passed by the Authority as complying with the Building Regulations subject to the following condition(s):

1.	Following examination of your submitted drawings and inspection of the map of sewers, it would appear that the proposal will be built over or within 3 metres of a public drain/sewer.  You are, therefore, required to consult with the owner of the drain/sewer or the statutory undertaker.

2.	Structural calculations are required to be deposited for the steelwork.

3.	The proposal has been identified as being in an area which may be affected by Radon.  Once the work has been completed, it is advisable that the property is tested in accordance with National Radiological Protection Board's recommendations.  Any cracks in the floor slab, walls, or at service entries are to be suitably sealed with flexible sealers.  A Radon tray is to be provided at GF d.p.c. level.

4.	The underfloor ventilation should be equivalent to 1500mm2 for each metre run of wall and be capable of providing cross ventilation to the complete floor area.

5.	The minimum U value for the extension wall element is 0.21 W/m2K.  Increase the insulation thickness or provide a U value calculation.

6.	The minimum U value for the extension pitched roof - insulation at ceiling level is 0.15 W/m2K.  Increase the insulation thickness or provide a U value calculation.

7.	Consequential improvements are required to the existing dwelling.  These could have an effect on the existing property and must be adhered to.  Firstly, note the comments in AD L1B (Wales) Section 4, page 15.  For details on 'consequential improvement measures' see the following references: Extensions less than 10m2, refer to pages 15 & 16, paras. 4.2.1 & 4.2.4.  For extensions over 10m2, refer to pages 15 & 16, paras. 4.2.1 & 4.2.4.  For extensions over 10m2, refer to pages 15 & 16, paras. 4.2.2 & 4.2.4.  Please provide details of your proposals to meet the criteria.  To access the document, please go to: http://wales.gov.uk/topics/planning/?lang=en.

8.	Indicate the ceiling joist sizes suitable for the span.

9.	Provide a layout plan showing the full details of the drainage system including runs, falls, invert levels, access and ventilation.  Full details of manhole construction and size.

10.	Provide installation and test certificates for the gas appliance.

11.	The cavities in the external wall must be effectively sealed at roof level.

This approval is only for the purposes of the requirements of the Building Regulations and Sections 19, 21, 23(3), 24 and 25 of the Building Act, 1984.  It is not an approval under the Town and Country Planning Acts, an approval for improvement grant purposes or for any other statutory provision.

Under the requirements of the Building Regulations the person carrying out the work to which the building regulations relate is required to notify the Authority at certain stages during the execution of the work.

Notification of inspections required, including commencement and completion inspections either by telephone / email / return slip (overleaf) will be acceptable.  In all cases please ensure you quote the reference number.  If work is not commenced within three years of submitting the plans the Authority may declare that the deposit of plans is of no effect under the provisions of the Building Act 1984, Section 32.

Following the first inspection of building works, a fee of £522.60 will be payable to the Council under the Building (Local Authority Charges) Regulations 2010.

PLEASE NOTE

Some forms of building work could invoke proceedings under The Party Wall etc. Act, 1996.  If you are uncertain of your position you are advised to consult a surveyor.

Dated: 9 January 2015

Director of Development Services

Address for all communications:

The Vale of Glamorgan Council,

Building Control,

Dock Office,

Barry Dock,

Barry.

CF63 4RT	Telephone No.  (01446) 704842

Under Statute you are obliged to adhere to the requirements of Regulation 16, as set out as attached, where applicable.

Building Inspection Request	2014/0864/BR

Please return this slip to advise the Authority when the work is ready to be inspected at commencement stage.

Location:	12, Romilly Avenue, Barry

Proposal:	Construct a two storey rear extension and rear ground floor balcony

Signature:		Date for Inspection:

Failure to inform the Authority may mean you will be required to uncover or remove work and could result In a fine.

Building Inspection Request	2014/0864/BR

Please return this slip to advise the Authority when the work is ready to be inspected at completion stage.

Location:	12, Romilly Avenue, Barry

Proposal:	Construct a two storey rear extension and rear ground floor balcony

Signature:		Date for Inspection:

Failure to inform the Authority may mean you will be required to uncover or remove work and could result In a fine.

THE BUILDING REGULATIONS 2010

REGULATION 16

Notice of commencement and completion of certain stages of work

16.

1.	A person carrying out building work shall give the Local Authority notice in writing, or by such other means as they may agree, of

(a)	the commencement of the work, at least 48 hours beforehand;

(b)	the covering up of any excavation for a foundation, any foundation, any damp-proof course or any concrete or other material laid over a site, at least 24 hours beforehand;

(c)	the haunching or covering up in any way of any drain or private sewer to which these regulations apply, at least 24 hours beforehand; and

(d)	the carrying out of any work of laying such drain or private sewer, including any necessary work of haunching or surrounding the drain or private sewer with concrete or other material and backfilling the trench, not more than seven days after it has been carried out.

2.	In the calculation of a period of hours for the purposes of paragraph (1)(a), (b) or (c), no account shall be taken of a Saturday, Sunday, Christmas Day, Good Friday, Bank Holiday or day appointed for public thanksgiving or mourning.

3.	If the person carrying out the work does not inform the Local Authority in accordance with paragraph (1), he shall comply with any notice in writing from the Local Authority requiring him within a reasonable time to cut into, lay open or pull down so much of the work as prevents the Local Authority from ascertain whether any of these regulations has been contravened.

4.	If the Local Authority have given notice in writing which specifies the manner in which any work contravenes the requirements in these regulations, a person who has carried out any further work to secure compliance with these regulations shall within a reasonable time after the completion of such further work give notice in writing to the Local Authority of its completion.

5.	A person carrying out work shall give the Local Authority notice in writing, or by such other means as they may agree, of -

(a)	the erection of a building, not more than seven days after completion, or (if a building or part of a building is occupied before completion) not less than seven days before occupation as well as not more than seven days after completion;

(b)	the completion of any other work, not more than seven days after such completion.

# Text boxes

9 January 2015

Mr. D. D. Williams

(01446) 704635

P/BC/2014/0864/BR/

BuildingControl@valeofglamorgan.gov.uk

## The Vale of Glamorgan Council

# Dock Office, Barry Docks,Barry  CF63 4RT

## Tel: (01446) 700111

TCyngor Bro Morgannwg

Swyddfa’r Doc, Dociau’r Barri, Y Barri CF63 4RT

Ffôn: (01446) 700111

www.valeofglamorgan.gov.uk

Date/Dyddiad:

Ask for/Gofynwch am:

Telephone/Rhif ffon:

Your Ref/Eich Cyf:

My Ref/Cyf:

e-mail/bost: