| To / I: | Yvonne Prichard |  | From / Oddi Wrth: | Faye Tomalin |
| --- | --- | --- | --- | --- |
| Dept / Adran: | Planning |  |  |  |
|  |  |  | My Ref / Cyf: | HE/SP/FET/L5/1 |
| Date / Dyddiad: | 16/05/2017 |  | Tel / Ffôn: | 02920 673 235 |
| Your Ref / Eich Cyf: | P/DC/LC/YVP/2017/00291/FUL |  | Fax / Ffacs: | 02920 673 114 |

Subject / Testyn:	Planning Application No. 2017/00291/FUL Greenyard Farm, Argae Lane, St Andrews Major

Proposal: Full planning application for the change of use of existing stone barna dn timber barn to residential, partial conversion of former milking parlour to garage uses, the demolition of the remaining milking parlour and steel framed buildings and erection of 12 holiday accommodation units and shower block

This site is not located within DAM zones at risk of tidal or fluvial flooding, and NRW flood maps indicate that there is a medium to low risk of surface water flooding to the adjacent highway.

No surface water drainage proposals have been submitted with this application. Although this application consists of a change of use for existing building on site, there is also an increase of impermeable area due to the addition of 12 holiday accommodation units. Therefore, prior to work commencing on site, a full surface water drainage plan shall be submitted to and approved by the LPA. Infiltration shall be the primary method of surface water disposal considered, prior to consideration of other method of surface water drainage techniques, therefore evidence of infiltration tests shall be required to be submitted. The scheme shall be designed so that flooding does not occur on any part of the site for a 1 in 30 year rainfall event plus climate change and not in any part of any building for the 1 in 100 year rainfall event plus climate change.

Should the use of SuDS techniques be used, a SuDS management plan shall be submitted to and approved by the LPA. This shall detail the strategy that will be followed to facilitate the optimal functionality and performance of the SuDS scheme throughout its lifetime.

Conditions:

Given the above, no development shall commence on site until a detailed scheme for the surface water drainage of the site, showing how road and roof / yard water will be dealt with has been submitted to and approved in writing by the Local Planning Authority. The scheme shall be designed so that flooding does not occur on any part of the site for a 1 in 30 year rainfall event plus climate change and not in any part of any building for the 1 in 100 year rainfall event plus climate change. Details shall include details of field percolation tests. Any calculation for onsite attenuation or discharge should also be included, along with full engineering details of drainage assets. The approved scheme must be implemented prior to beneficial occupation and as built drawings should be submitted to the LPA.  This is to ensure that effective drainage facilities are provided for the proposed development and that flood risk is not increased elsewhere.

No works or development shall take place until a SuDS management plan which includes details on future management responsibilities for the site and its drainage assets has been submitted and approved in writing by the Local Planning Authority. This plan shall detail the strategy that will be followed to facilitate the optimal functionality and performance of the SuDS scheme throughout its lifetime. The management plan shall be implemented in full accordance with the agreed terms and conditions in perpetuity.

Faye Tomalin

Engineering Assistant (FCERM)

for Operational Manager Highways and Engineering

ar ran Rheolwr Gweithredol Priffyrdd a Pheirianneg