| To / I: | Head of Planning and Transportation |  | From / Oddi Wrth: | Operational Manager Highways and Engineering |
| --- | --- | --- | --- | --- |
| Dept / Adran: |  |  |  |  |
|  |  |  | My Ref / Cyf: | HE/SP/CRM/L5/1 |
| Date / Dyddiad: | 25/07/2017 |  | Tel / Ffôn: | 029 20673277 |
| Your Ref / Eich Cyf: | P/DC/LC/YP/ |  | Fax / Ffacs: | 029 20673114 |

Subject / Testyn: Planning Application 2017/00724/RERS Caerleon Road, Dinas Powys

Proposal: Approval of all Reserved Matters on outline consent 2014/00282/OUT

This site is not located in DAM areas at risk of tidal or fluvial flooding, and NRW maps indicate that there is a low risk of surface water flooding to some areas of the site. This area of low surface water flood risk is sited in the approximate location of a historical watercourse on the site, and this should therefore be considered by the developer. This site is situated above a known flood risk area (Brookside area of Dinas Powys) and as a result NRW should be consulted on this matter. It is, therefore, also important to ensure that development of this site does not exacerbate flood risk in the surrounding areas.

The drainage plan submitted indicates that all surface water will be disposed of via an attenuation basin and a new connection into an existing public surface water sewer through private gardens. Any connection to the public surface water sewer will be required to be approved by Dŵr Cymru Welsh Water, and they should therefore be consulted on this application.

The primary method of surface water disposal should be infiltration and this should be considered prior to any other method. The Drainage Strategy submitted with the outline application indicates that soakaway tests have been carried out on this site and disposal of surface water via infiltration is not possible across the site, although evidence of these soakaway tests have not been included with this application.

Hydraulic calculations have not been submitted to demonstrate that the efficiency of the whole proposed drainage system across the site. The drainage system should be designed so that no part of the site floods for the 1 in 30 year design storm event, and no building floods to the 1 in 100 year design storm, plus 30% for climate change.

Full engineering details of the proposed attenuation basin have also not been submitted with this application. Prior to work commencing on site, full engineering details of the proposed design scheme shall be submitted to, and approved by the LPA.

The Drainage Strategy submitted with the outline application indicated that the drainage features on site will be adopted by the relevant SuDS Approval Body (SAB). No SAB’s are currently in place, and no further information has been submitted with this Reserved Matters application. Therefore, the applicant should provide a management and maintenance plan that details the strategy that will be followed to facilitate the optimal functionality and performance of the SuDS scheme throughout its lifetime.

Conditions:

Given the above, no development shall commence on site until a detailed scheme for the surface water drainage of the site, showing how road and roof / yard water will be dealt with has been submitted to and approved in writing by the Local Planning Authority. Evidence of infiltration testing and any calculation for onsite attenuation or discharge should also be included. The approved scheme must be implemented prior to beneficial occupation and as built drawings should be submitted to the LPA.  This is to ensure that effective drainage facilities are provided for the proposed development and that flood risk is not increased elsewhere.

In connection with the condition above, the detailed scheme for drainage shall identify all existing surface water drainage structures within the site and demonstrate that they are still utilised for their intended use, or that alternative provision is made.  The scheme shall also demonstrate that flows within said structures, and across the site, are maintained during construction works and thereafter.

A written declaration is required detailing responsibility for the adoption and maintenance of all elements of the drainage system prior to beneficial occupation.  A maintenance schedule for the surface water system should be submitted to and approved in writing by the Local Planning Authority prior to development commencing.  The developer shall provide as‐built drawings for the surface water drainage system to the Local Planning Authority.

F. Tomalin

Engineering Assistant (FCERM)

for Operational Manager Highways and Engineering

ar ran Rheolwr Gweithredol Priffyrdd a Pheirianneg