| To / I: | Development Services |  | From / Oddi Wrth: | Operational Manager Highways and Engineering |
| --- | --- | --- | --- | --- |
| Dept / Adran: |  |  |  |  |
|  |  |  | My Ref / Cyf: | HE/SP/CRM/L5/1 |
| Date / Dyddiad: | 12/09/2017 |  | Tel / Ffôn: | 029 20673277 |
| Your Ref / Eich Cyf: | P/DC/LC/SDB/2015/00392/OUT |  | Fax / Ffacs: | 029 20673114 |

Subject / Testyn:	Planning Application No. 2015/00392/OUT Land at Cardiff Road/Cross Common Road, Dinas Powys

Condition 6: Notwithstanding the submitted details and prior to the commencement of works on site, further details of a scheme for foul and surface water drainage shall be submitted to and approved in writing by the Local Planning Authority, which shall ensure that foul water and surface water discharges shall be drained separately from the site, with no surface water or land drainage run-off allowed to connect (either directly or indirectly) into the public sewerage system.  This should include details of anticipated discharge rates and connections with adjacent watercourses. The approved scheme shall be fully implemented in accordance with the approved details prior to first beneficial occupation of any of the dwellings hereby approved.

The following plans have been submitted in order to discharge this condition:

- 10157-001 A Engineering Layout

- Drainage Statement June 2017

- Planning Layout 1628-100 A

The engineering layout provided indicates that surface water shall be disposed of via an attenuation basin and swale system. It demonstrates that surface water flow paths across the development have been considered. The engineering layout shows highway connections to the surface water drainage system; however roof/yard water connections are not indicated at this stage.

The engineering layout and the planning layout indicate that an existing ditch at the southern boundary of the site is to be retained. It should be demonstrated that is adequate access to this ditch for maintenance purposes.

Engineering details shall also be provided on the attenuation basin and swales that will be used across the site. This shall include cross-sections and long-sections, along with storage volumes and depths.

The drainage statement states that the max discharge from the site will be 14l/s. Further justification of this rate of discharge is required to be submitted. The contributing catchment to this development site is stated to be 22.4 Ha. A plan showing the extent of this catchment is required to be submitted prior to discharge of any drainage condition associated with this site.

No information has so far been provided on the standard of service that this surface water drainage system shall provide. Therefore, prior to discharge of condition, hydraulic calculations shall be submitted demonstrating that the surface water drainage system shall not cause any part of the site to flood for the 1 in 30 year design event, and no building shall flood to the 1 in 100 year design event with a 30% allowance for climate change. Hydraulic calculations shall also take into consideration hydraulic locking of the outfall of the drainage system within the Cadoxtan River. A plan indicating exceedance flow routes and depths shall also be submitted in order to discharge this condition.

Prior to discharge of the condition, a Health and Safety Report should also be submitted. This report shall identify the risks to pedestrians and vehicles from the drainage system to be implemented, and identify how these risks shall be mitigated through design and on site.

No SuDS maintenance plan has been submitted with this application. Therefore, prior to discharge of this condition, a plan detailing the measures that shall be put in place to ensure optimum functionality of the drainage system for the lifetime of the development shall be submitted and approved by the LPA.

Therefore, this section objects to the discharge of Condition 6 of planning application 2015/00392/OUT until sufficient information has been submitted to and approved by the LPA. This information is to include:

- Full engineering details of the surface water drainage system, including cross-sections

- Hydraulic calculations demonstrating the standard of service that the system shall provide, along with consideration of hydraulic locking of the system from the Cadoxtan River

- Exceedance flow routes across the site

- Health and Safety report identifying the risks of the drainage system to pedestrians and vehicles

- SuDS Management and Maintenance Plan

F. Tomalin (Engineering Assistant – FCERM)

for Operational Manager Highways and Engineering

ar ran Rheolwr Gweithredol Priffyrdd a Pheirianneg