| To / I: | Yvonne Prichard |  | From / Oddi Wrth: | Faye Tomalin |
| --- | --- | --- | --- | --- |
| Dept / Adran: | Planning |  |  |  |
|  |  |  | My Ref / Cyf: | HE/SP/FET/L5/1 |
| Date / Dyddiad: | 03/01/2018 |  | Tel / Ffôn: | 02920 673 235 |
| Your Ref / Eich Cyf: | P/DC/LC/YVP/2017/01241/FUL |  | Fax / Ffacs: | 02920 673 114 |

Subject / Testyn:	Planning Application No. 2017/01241/FUL 75 Cardiff Road, Dinas Powys

Proposal: Demolition of Existing building. Construction of retail unit with new access, parking and refuse facilities

NRW maps indicate that there is a low to medium risk of surface water flooding to the highway adjacent to the site.

No surface water drainage plan has been submitted with this application, however the application form indicates that surface water will be disposed via the mains sewer. Infiltration should the primary method of surface water disposal prior to any other method being considered. This is in accordance with the Non-Statutory SuDS Guidelines for Wales. Therefore, prior to work commencing on site a full drainage plan shall be submitted to and approved by the LPA. The drainage plan shall include evidence of onsite porosity testing and hydraulic calculations demonstrating the proposed standard of service that the proposed drainage system shall provide. The drainage system shall ensure that no part of the site shall flood to the 1 in 30 year design storm, and no part of the site shall flood to the 1 in 100 year design storm plus 30% for climate change.

Should the use of SuDS techniques be used, a SuDS management plan shall be submitted to and approved by the LPA. This shall detail the strategy that will be followed to facilitate the optimal functionality and performance of the SuDS scheme throughout its lifetime.

Conditions:

Given the above, no development shall commence on site until a detailed scheme for the surface water drainage of the site, showing how road and roof / yard water will be dealt with has been submitted to and approved in writing by the Local Planning Authority. Details shall include details of field percolation tests. Any calculation for onsite attenuation or discharge should also be included, along with full engineering details of drainage assets. A management plan for the on-going maintenance of the system shall also be included. The approved scheme must be implemented prior to beneficial occupation and as built drawings should be submitted to the LPA.  This is to ensure that effective drainage facilities are provided for the proposed development and that flood risk is not increased elsewhere.

Faye Tomalin

Engineering Assistant (FCERM)

for Operational Manager Highways and Engineering

ar ran Rheolwr Gweithredol Priffyrdd a Pheirianneg