Vale of Glamorgan County

Dock Office

Holton Road Barry Docks

Barry

CF63 4RT

|  | Date: 14/03/2023 |
| --- | --- |
|  | Our Ref: PLA0071395 |
|  | Your Ref: 2023/00051/HYB |

# Dear Sir/Madam

Grid Ref: ST112672 311552 167357

Site: No.1 Dock and The Mole,  Neptune Road, Barry Waterfront, Barry,

Development: The proposals for the site are the subject of a hybrid application and are made up of five distinct, but complementary, components as follows: See app for full details

We refer to your planning consultation relating to the above site, and we can provide the following comments in respect to the proposed development.

SEWERAGE

We have reviewed the information submitted as part of this application and note that a drainage strategy has not been submitted to show how foul water will be disposed of.

Therefore, if you are minded to grant planning permission we request that the following Conditions and Advisory Notes are included within any subsequent consent.

Conditions

No development shall commence until a drainage scheme for the site has been submitted to and approved in writing by the local planning authority. The scheme shall provide for the disposal of foul, surface and land water, and include an assessment of the potential to dispose of surface and land water by sustainable means. Thereafter the scheme shall be implemented in accordance with the approved details prior to the occupation of the development and no further foul water, surface water and land drainage shall be allowed to connect directly or indirectly with the public sewerage system.

Reason: To prevent hydraulic overloading of the public sewerage system, to protect the health and safety of existing residents and ensure no pollution of or detriment to the environment.

Advisory Notes

In accordance with Planning Policy Wales (Edition 11) and Technical Advice Note 12 (Design), the applicant is advised to take a sustainable approach in considering water supply in new development proposals, including utilising approaches that improve water efficiency and reduce water consumption. We would recommend that the applicant liaises with the relevant Local Authority Building Control department to discuss their water efficiency requirements.

The proposed development may be subject to Schedule 3 of the Flood and Water Management Act 2010. The development therefore may require approval of Sustainable Drainage Systems (SuDS) features, in accordance with national standards, and is strongly recommended that the developer engage in pre-application consultation with the Local Authority, as the relevant SuDS Approval Body (SAB) .

The applicant may need to apply to Dwr Cymru / Welsh Water for any connection to the public sewer under S106 of the Water industry Act 1991. If the connection to the public sewer network is either via a lateral drain (i.e. a drain which extends beyond the connecting property boundary) or via a new sewer (i.e. serves more than one property), it is now a mandatory requirement to first enter into a Section 104 Adoption Agreement (Water Industry Act 1991). The design of the sewers and lateral drains must also conform to the Welsh Ministers Standards for Gravity Foul Sewers and Lateral Drains, and conform with the publication "Sewers for Adoption"- 7th Edition. Further information can be obtained via the Developer Services pages of www.dwrcymru.com

The applicant is also advised that some public sewers and lateral drains may not be recorded on our maps of public sewers because they were originally privately owned and were transferred into public ownership by nature of the Water Industry (Schemes for Adoption of Private Sewers) Regulations 2011.  The presence of such assets may affect the proposal.  In order to assist us in dealing with the proposal the applicant may contact Dwr Cymru Welsh Water on 0800 085 3968 to establish the location and status of the apparatus. Under the Water Industry Act 1991 Dwr Cymru Welsh Water has rights of access to its apparatus at all times.

WATER SUPPLY

The water supply system in the immediate vicinity has insufficient capacity to serve the development and will also cause detriment to existing customers’ water supply. The applicant is advised that as part of any future water connection application under Section 41 of the Water Industry Act (1991), a hydraulic modelling assessment and the delivery of reinforcement works may be required at the same time as the provision of new water mains to serve the new development under Section 41 and Section 51 of the Water Industry Act (1991).

Our response is based on the information provided by your application.  Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.

If you have any queries please contact the undersigned on 0800 917 2652 or via email at developer.services@dwrcymru.com

Please quote our reference number in all communications and correspondence.

# Yours faithfully,

# Chris Scourfield

# Development Planning Officer

# Developer Services